## Slide 1: Quantitative Resiliency Analysis of Microgrids
Myron Hecht
The Aerospace Corporation
Presented to
INCOSE International Workshop
Jacksonville, FL
February, 2018
2017

## Slide 2: Outline
Motivation
Quantitative Resiliency Definition
Application
Matlab model
SysML Model
Results
Discussion
Conclusions

## Slide 3: Motivation
Resiliency lacks a specific quantitative definition and associated metrics that enable assessment [1]
This work shows a Model Based Systems engineering (MBSE), and in particular SysML [2] and Markov models [3], can be used to assess resiliency

## Slide 4: Quantitative Definition of Resiliency
Resiliency is the probability weighted sum of MOPs in each system state
Where
Rs is the system resiliency measure
Pk is the probability of being in state k
MOPk is the measure of performance for that state (Power generated, Power relative to demand, Total Energy Delivered)

## Slide 5: Remarks
Use of states is consistent with earlier approaches to resilience [4]
The definition can be applied to any system which meets the following conditions
  Systems can be characterized by states (normal, multiple degraded states, totally disabled states)
  There is an ascertainable probability of being in each State
    The probability need not be directly measurable if it can determined on the basis of other measurable parameters
  Each state has at least one quantifiable Measure of Performance (MOP) which is of interest to the stakeholders

## Slide 6: Equivalent to alternative definition from the IEEE-CS/ INCOSE System Engineering Book of Knowledge [5]
R= resilience required of the capability
N= number of states
n = the number of exhaustive and mutually exclusive adversity scenarios or states
Pi = the probability of adversity scenario or state i;
Cr(t)i = The numerical effectiveness (between 0 and 1) of the capability in the scenario or state
T = length of the time of interest.
substitute
then
Comment: The SEBOK formulation of MOP defines an average capability over the time interval (0,T) for a time varying capability function (Cr) in state i
SEBoK definition
(definition proposed on previous chart)

## Slide 7: Application: Microgrids
A microgrid is a group of interconnected loads and distributed energy resources within clearly defined electrical boundaries that contains loads, distributed energy sources
Microgrids are a key element in increasing the resiliency of the electrical grid
Microgrids have multiple states:
  Connected (normal state)
  Island/generator power
  Island/battery power
  No power

## Slide 8: Application: Microgrid Resiliency (1/2)
Three Measures of Performance (MOPs) of interest to stakeholders
    Power generation capacity (PG)
    Power generation capacity vs. demand (PD / PG)
    Total Energy Provided: (EP =A PG t)
      A=Availability of Power
      t = Time
      Energy = Power *Time
Terminology issue: in this system, there are multiple possible MOPs, we refer to each probability weighted sum as a resiliency measure,

## Slide 9: Example
State | Proba-bility | Measures of Performance (MOPs) |  |  | Probability Weighted MOPs |  | 
 |  | Power Genera-tion Capacity (KW) | Capacity vs. Demand | Energy Provided (KWH, 100 hours) | Capacity | Capacity vs. Demand | Energy Provided
Utility Power (U) | 0.9581 | 4000 | 1 | 400,000 | 3832.4 | 0.9581 | 383240
Generator Power (G) | 0.0261 | 2400 | 0.6 | 240,000 | 62.64 | 0.01566 | 6264
Battery Power (B) | 0.0105 | 2000 | 0.5 | 200,000 | 21 | 0.00525 | 2100
No Power (N) | 0.0054 | 0 | 0 | - | 0 | 0 | 0
Resiliency Measure |  |  |  |  | 3,916 | 0.9790 | 391,604

## Slide 10: SysML Block Definition diagram

## Slide 11: Microgrid Blocks
Block | Description
Consumers | Customers of the microgrid (electrical power users)
Microgrid Domain | Domain of the microgrid including components, stakeholders, and threats
Microgrid | A group of interconnected loads and distributed energy resources within clearly defined electrical boundaries that contains loads, distributed energy sourc
Threats | Phenomena (natural or anthropogenic) that can degrade or destroy the availability of power to consumers
Stakeholders | stakeholders in the microgrid (consumers, technicians, utility management, microgrid management)
Storage | Electrical energy storage (battery) characterized by a capacity (watt-hours)
Generators | System elements that convert other forms of energy into electrical power with the load (diesel generators, gas turbines, solar arrays, windmills)
Utility | The external grid to which the microgrid is connected
Interconnect switch | A device which connects the microgrid to the utility
Load | Aggregate of power consumers on microgrid measured in watts

## Slide 12: SysML Internal Block diagram

## Slide 13: Parametric Diagram

## Slide 14: Mathematical Model Assumptions
Resilient Component behavior
  Any component can fail
  Any component can be subject to a cyberattack
  Failed components can be restored
    Restoration times can be modeled
Microgrid behavior
  Interconnect switch necessary to isolate microgrid from the main grid
  Diesel Generators have a limited fuel supply
    Refueling waiting time can be modeled
  Gas turbines are subject to natural gas cutoff
  Solar cells require daylight to generate power
  Batteries have a limited capacity which is subject to a demand
  Demand is variable and controllable within the power grid
Mathematics
  Times between failures and recovery times are distribution exponentially
  Component failures are independent of each other

## Slide 15: State Transition Diagram
Steady State Markov Model solution provides the percentage of time that the system is in each state (state residence probability)

## Slide 16: Input Variables
Name | Owning Block | Meaning
Ct | Generator | Capacity of fuel tank in liters
F | Generator | Fuel consumption rate for diesel generator set (liters per hour)
L_gen | Generator | diesel generator set failure rate
m_gen | Generator | repair rate for generator
Pgen | Generator | Probabaility of successful generator startup
L_inter | Interconnet | Failure rate of interconnect switch
m_inter | Interconnet | repair rate of the interconnect switch
Pinter | Interconnet | Probability of successful interconnect switching to island mode upon interruption of utility power
demand | Load | Demand of load (in watts)
c_bat | Storage | Capacity of battery
L_bat | Storage | Failure rate of battery (or other electrical energy storage device)
m_bat | Storage | Repair rate of battery (or other electrical energy storage device)
L_emp | threats | Occurrence rate of electromagnetic pulses (EMP) sufficient to disable the utility
L_xtreme | threats | Occurrence rate of extreme weather conditions (aggregate)
m-cyber | threats | recovery rate from microgrid cyberattack
L_norm | Utility | Failure rate (interruption rate) of the grid
m_norm | Utility | Weighted average recovery time of common repairs, extreme weather repairs, EMP, and cyber reapirs
L_gen | Generator | diesel generator set failure rate
m_gen | Generator | diesel generator set restoration rate
Pgen | Generator | probability of successful diesel generator start on demand

## Slide 17: Variables used in this analysis
Input | Meaning | Value | Units
L_util | Utility outage frequency | 0.001 | per hour
L_cyber | Utility cyberattack rate | 0.0001 | per hour
Pinter | Probabiltiy of successful interconnect switch | 0.999 | none
m_util | Utility restoration rate | 0.05 | per hour
Pgen | Probability of successful generator start | 0.99 | none
L_gen | Generator failure rate | 0.001 | per hour
m_gen | Generator restoration rate | 0.025 | per hour
F | Fuel consumption rate in liters per hour | 1000 | liters per hour
Ct | capacity of fuel tank | 2.40E+05 | liters
L_bat | battry failure rate | 0.001 | per hour
m_bat | battery repair rate | 0.025 | per hour
Load | demand on battery in Watts | 1000 | per hour
Cb | battery capacity in watt hours | 20000 | Watts

## Slide 18: Matlab Function for Constraint Block Microstead1
function [PU1, PG1, PB1, PN1, PU2, PG2, PB2, PN2] = microstead1( L_util, L_cyber, Pinter, m_util, Pgen, L_gen, m_gen, L_bat, m_bat, F, Ct, Load, Cb)
%Function Microstead1
%M. Hecht 10/24/2017
% Steady State solution Microgrid
%Transition Expressions
E11=-L_util-L_cyber*Pinter -Pinter*Pgen*(L_util+L_cyber);
E21=Pinter*Pgen*(L_util+L_cyber);
E22= -Pgen*(L_cyber+F/Ct+L_gen)-L_gen*(1-Pgen)-m_util;
E31=Pinter*(1-Pgen)*(L_util+L_cyber);
E32=Pgen*(L_cyber+F/Ct+L_gen);
E33=-L_cyber-L_bat-Load/Cb-m_gen;
E41=L_util*(1-Pinter);
E42=L_gen*(1-Pgen);
E43=L_cyber+L_bat+Load/Cb;
E44=-m_util-m_bat-m_gen;
T1=[ 1 1 1 1;
E11 m_util m_util m_util;
E21 E22 m_gen m_gen;
E41 E42 E43 E44];
P=[1 0 0 0 ]';
b1=inv(T1)*P;
PU1=b1(1);
PG1=b1(2);
PB1=b1(3);
PN1=b1(4);
end

## Slide 19: Selected Results: . Impact of Successful Cyberattack Rate

## Slide 20: Selected Results: Impact of Utility Power Outage Rate

## Slide 21: Selected Results: Impact of Utility Restoration Rate

## Slide 22: Discussion
Usefulness: conclusions that can be reached using this model
  Successful cyberattack rate is the most significant parameter
  Utilities should strive to keep their average restoration time after an outage to 10 hours (below that, not much significant benefit; above that , disproportionate benefit)
Limitations:
  Considers only continuous time events, not discrete events such as battery discharged, diesel storage tanks refilled, etc.
  Model has only one load and one generator
  Assumption of exponential assumption (doesn’t model running out of fuel or a battery being drained of energy)
  Load shedding not considered
  Input parameter values are not verified
  The specific analytical model and results are shown for the purposes of illustration of this point. Not intended to be generalized to other systems
All Models are Wrong, Some Models are Useful

## Slide 23: Conclusions
Quantitative Metrics for Resiliency Can Be Developed
  Necessary to evaluate current designs, alternatives, and tradeoffs
MBSE can incorporate resiliency analyses
  Models can provide the metrics
  Such models can enable design decisions
Next Steps for Microgrid Resiliency Model
  Incorporate into INCOSE Critical Infrastructure Protection and Recovery (CIPR) Working Group
    Already achieved in collaboration with S. Friedenthal
  Refine models to account for extreme events and EMP with separate parameters
  Add models for solar arrays and gas turbines
  Add multiple loads and generators to state transition diagrams
  Investigate use of discrete event simulators

## Slide 24: References
[1] National Academies of Sciences, Engineering, and Medicine , Enhancing the Resilience of the Nation's Electricity System , available online at http://www.nap.edu/, p. 10 (2017)
[2] Object Management Group, “System Modeling Language”, www.sysml.org, specification available at http://sysml.org/sysml-specifications/ (2015)
[3] , Alberto Avritzer, Daniel S. Menasch Javier Alonso, Leandro Aguiar, and Sara G. Alvarez, "WAP: Models and Metrics for the Assessment of Critical-Infrastructure-Targeted Malware Campaigns," in International Symposium on Software Reliability Engineering, Gaithersburg, MD, (2015).
[4] Scott Jackson, Stephen Cook, and Timothy L. J. Ferris, “A Generic State-Machine Model of System Resilience”, Insight Magazine, April, 2015, pp. 14-18
[5] Resilience Engineering in System Engineering Book of Knowledge version 1.8, http://sebokwiki.org/wiki/Resilience_Engineering, Systems Engineering Research Center (SERC), the International Council on Systems Engineering (INCOSE), and the Institute of Electrical and Electronics Engineers Computer Society (IEEE-CS) March 2017